# ANNEX B – Energy Audit Report For Building Cooling System

Date: DD/MM/YEAR

ENERGY AUDIT REPORT FOR BUILIDNG COOLING SYSTEM

FOR

ENTER BUILDING NAME

Submitted By

Enter name of PE/Energy Auditor

PE (Mech) Registration No*: Enter No.

Energy Auditor Registration No*: Enter No.

*Delete whichever is not applicable

Contents

1.0	Building Information	21

2.0	Energy Audit Information For Building Cooling System	21

2.1	Chilled Water Plant information*	22

2.2	Chilled Water Plant Normal Operating Hours	23

3.0	Instrumentations	23

4.0	Chiller Plant Performance Analysis	24

4.1	Summary of Chilled Water Plant Performance	26

5.0	Summary of Heat Balance	26

Table 1: Chiller Information (Example)	22

Table 2: Ancillary equipment Information (Example)	22

Table 3: Instrumentation Table (Example)	23

Table 4: Heat Balance Summary	27

Figure 1: Super-imposed plot of daily Cooling Load Profile (Example)	24

Figure 2: Histogram of Cooling Load Occurrences (Example)	24

Figure 3:Super-imposed plot of daily chiller plant efficiency (Example)	25

Figure 4: Scatter plot of chiller plant efficiency over cooling load (Example)	25

Figure 5: System Level Heat Balance Plot (Example)	26

# 1.0	Building Information

Enter a brief description of the building here.

Project Reference Number	: Enter project reference indicated in CORENET submission

Building Name			:

Building Address		:

Postal Code			:

Building Type			:

Building Age			:

Date of last Energy Audit Submission	:

Gross floor area (GFA), m2	:

Air conditioned area, m2	:

# 2.0	Energy Audit Information For Building Cooling System

Enter PE(Mech)(Mechanical)/ Energy Auditor Name was appointed by Enter Owner Name/ MCST, owner of Enter Building Name to be the Energy Auditor for the 3 yearly submission of the operating system efficiency (OSE) of the centralized Chilled Water Plant. The report will present the performance of centralized Chilled Water Plant efficiency based on the measurements from the permanent instrumentations installed on site.

Location 			:	 Enter location of Chilled Water Plant

Energy Audit Period		: 	Enter  Energy Audit period *Note: Minimum 1

week

Date of notice served		:	Enter date of notice served by BCA

Date of submission in notice	: 	Enter submission deadline stipulated in BCA notice

Data Logging Interval		:	1 minute sampling

Trend Logged Parameters*	:	Chilled Water Supply main header temperature

Chilled Water Return main header temperature

Chilled Water flow rate at chilled water return main header

Condenser Water Supply main header temperature

Condenser Water Return main header temperature

Condenser water flow rate at condenser water return main header

Power input to Chiller(s)

Power input to Chilled water pump(s)

Power input to Condenser water pump(s)

Power input to Cooling tower(s)

* Trend logged parameters are not limited to the above and may vary depending on the piping and electrical circuit design.

# 2.1	Chilled Water Plant information*

Table 1: Chiller Information (Example)

| ID | Description | Type | Name plate motor (kW) | Cooling Capacity (RT) | Chilled water LWT | Chilled water ∆T | Rated Efficiency kW/RT | Year Installed |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CH01 | Chiller 1 | Centrifugal | 150 | 1000 | 6.7 °C | 5.5°C | 0.55 | 2012 |
| CH02 | Chiller 2 | VSD Screw | 90 | 500 | 6.7 °C | 5.5°C | 0.52 | 2012 |

| ID | Description | Name plate motor (kW) | Pump Head (m) | Flow rate (L/S) | Rated Pump/ Fan efficiency | Rated Motor Efficiency |
| --- | --- | --- | --- | --- | --- | --- |
| CHWP01 | Chilled water pump 1 | 55 | 30 | 151.2 | 85% | 95% |
| CHWP02 | Chilled water pump 2 | 30 | 30 | 75.6 | 85% | 95% |
| CWP01 | Condenser water pump 1 | 45 | 20 | 189 | 85% | 95% |
| CWP02 | Condenser water pump 2 | 22 | 20 | 94.5 | 85% | 95% |
| CT01 | Cooling tower 1 | 45 | - | 130 | 75% | 92% |
| CT02 | Cooling tower 2 | 45 | - | 130 | 75% | 92% |

Table 2: Ancillary equipment Information (Example)

*Based on equipment design specifications and name plate ratings.

## 2.2	Chilled Water Plant Normal Operating Hours

Monday to Friday		: 	0730 – 1900 Hrs

Saturday			: 	No operations

Sunday				: 	No operations

Note: The operating hours should follow the table in clause 6.1.4

# 3.0	Instrumentations

Accurate measuring instruments complying with the Code on Environmental Sustainability Measures for Existing Buildings or the Code for Environmental Sustainability of Buildings (2nd edition and onwards) that is prevailing at the time of installation were used during the audit to gather information on the power consumption, temperatures and flow rate.

The points of measurements are listed in the following table:

| ID | Description | Sensor Type | Installation Location | Measurement/ Calibration range | Measurement Uncertainty (%) | Last Calibration Date |
| --- | --- | --- | --- | --- | --- | --- |
| TT01 | CHWS Temperature | 10K Ω Thermistor | CHWS Header | 0°C - 40°C | ±0.03 °C | 15/10/2012 |
| TT02 | CHWR Temperature | 10K Ω Thermistor | CHWR Header | 0°C - 40°C | ±0.03 °C | 15/10/2012 |
| TT03 | CWS Temperature | 10K Ω Thermistor | CWS Header | 0°C - 40°C | ±0.03 °C | 15/10/2012 |
| TT04 | CWR Temperature | 10K Ω Thermistor | CWR Header | 0°C - 40°C | ±0.03 °C | 15/10/2012 |
| FM01 | CHW Flow | Magnetic Full Bore | CHWR Header | 30 l/s- 200 l/s | 0.5% | 20/10/2012 |
| FM02 | CW Flow | Magnetic Full Bore | CWR Header | 30 l/s- 200 l/s | 0.5% | 20/10/2012 |
| kW01 | Chiller 1 Power | True RMS, 3 phase | ACMSB1 | 60 – 600 kW | 0.5% | 30/10/2012 |
| kW02 | Chiller 2 Power | True RMS, 3 phase | ACMSB2 | 60 – 600 kW | 0.5% | 30/10/2012 |
| kW03 | CHW Pump 1 & 2 Power | True RMS, 3 phase |  | 20 – 200 kW | 0.5% | 30/10/2012 |
| kW04 | CW Pump 1 & 2 Power | True RMS, 3 phase | CHW SB | 20 – 200 kW | 0.5% | 30/10/2012 |
| kW05 | CT 1 & 2 Power | True RMS, 3 phase | CT Panel | 15 – 150 kW | 0.5% | 30/10/2012 |

Table 3: Instrumentation Table (Example)

# 4.0	Chiller Plant Performance Analysis

Figure 1: Super-imposed plot of daily Cooling Load Profile (Example)

Figure 2: Histogram of Cooling Load Occurrences (Example)

Figure 3:Super-imposed plot of daily chiller plant efficiency (Example)

Figure 4: Scatter plot of chiller plant efficiency over cooling load (Example)

## 4.1	Summary of Chilled Water Plant Performance

|  | Efficiency | Unit |
| --- | --- | --- |
|  | Daytime^ | Night-time~ |  |
| Chiller(s) efficiency |  |  | kW/RT |
| Chilled water pump(s) efficiency |  |  | kW/RT |
| Condenser water pump(s) efficiency* |  |  | kW/RT |
| Cooling tower(s) efficiency* |  |  | kW/RT |
| Overall chiller plant efficiency |  |  | kW/RT |

*Not applicable to air-cooled Chilled Water Plant

~For hotels and other developments with 24-hour operations only; Night-time shall refer to the period from 11pm – 7am;

^ For hotels and other developments with 24-hour operations, day-time shall refer to the period from 7am – 11pm; for all other developments, daytime shall refer to the normal operating hours stipulated in clause 6.1.4

# 5.0	Summary of Heat Balance

Figure 5: System Level Heat Balance Plot (Example)

|  | Quantity | Unit | Formula |
| --- | --- | --- | --- |
| Sum of total electrical energy used |  | kWh | (A) |
| Sum of total cooling produced |  | RTh | (B) |
| Sum of total heat rejected |  | RTh | (C) |
| Chiller Plant Efficiency |  | kW/RT | (A) / (B) |
| Total Heat Balance Data Count |  | - | (D) |
| Data Count > + 5% error |  | - | (E) |
| Data Count < - 5% error |  | - | (F) |
| Data Count within ±5% error |  | - | (G) = (D) – (E) – (F) |
| % Heat Balance within ±5% error |  | % | 100 x (G) / (D) |

Table 4: Heat Balance Summary

# Text boxes

0.79%

32.19% %

8.54 %

14.35 %

42.85 %

1.28 %

± 5%